Design and Development of an Automated Test Bench for Robustness Testing of Teleprotection Equipment in Electrical Substations

Sergio Bret Villalta

Project Critical Review

REVISION HISTORY AND APPROVAL RECORD

| Revision | Date | Purpose |
| --- | --- | --- |
| 0 | 27/11/2025 | Document creation |
| 1 | 28/11/2025 | Document revision |

DOCUMENT DISTRIBUTION LIST

| Name | E-mail |
| --- | --- |
| Sergio Bret Villalta | sergio.bret@estudiantat.upc.edu |
| Viente Jimenez Serres - UPC tutor | vicente.jimenez@upc.edu |
| David Gil Donate – Entity tutor | DAVID.GIL@ZIVAUTOMATION.COM |

| WRITTEN BY: Sergio Bret Villalta 1 |  |  | REVIEWED AND APPROVED BY: |  |  |
| --- | --- | --- | --- | --- | --- |
| Date | 30/11/2025 |  | Date |  |  |
| Name | Sergio Bret Villalta |  | Name |  |  |
| Position | Project author |  | Position |  |  |

# Contents

0.	Contents	3

1.	General comments about the work progress	4

1.1.	Incidences	4

1.2.	Work Plan modifications	5

2.	updated work plan	6

2.1.	Updated Work Packages, Tasks and Deliverables	6

2.2.	Updated Time Plan (Gantt diagram)	9

# General comments about the work progress

## Incidences

During the execution of WP2 (Design and Construction of the HIL Test Bench), a critical integration issue arose between the Raspberry Pi GPIOs and the TPU-1 hardware interfaces, specifically regarding the Command Output reading ($TPU \rightarrow RPi$).

- Impedance Mismatch and Leakage Current: The TPU-1 output modules utilize Solid State Relays (SSR). It was diagnosed that these SSRs have a leakage current of approximately $300\mu A$ in the open state1.

- Signal Saturation: The Raspberry Pi's internal pull-up resistors (~50k$\Omega$) were insufficient to drain this leakage current. According to Ohm's Law, this resulted in a voltage drop of $\approx 15V$ (theoretical), keeping the logic level in an indeterminate state2.

- Noise Susceptibility: This high-impedance floating state caused the RPi to detect massive electromagnetic noise, registering over 4.6 million false events in seconds3, rendering the test bench unusable for precise timing measurements.

- Solution: Direct connection was ruled out. A hardware redesign is required to include an Optocoupler Interface Module. This will provide galvanic isolation and a low-impedance current sink (>5mA activation threshold) to filter out the SSR leakage and stabilize the reading4.

Mencionar también:

PROBLEMA DE SINCRONISMO

Contexto:

- Pruebas de rendimiento, mostrando los retardos en diferentes partes de la transmisión en una iteración de pulsos (generación de Inputs) en un escenario End To End con dos equipos conectados con una linea de transmisión con cable rj45 mediante módulos de comunicación digitales ICPT. Para mostrar los retardos, necesitamos obtener los timestamps en los que se producen los siguientes eventos:

  - T0: Instante en el que se produce la señal de accionamiento de los relés mediante canal de feedback a través de optoacopladores tomando la salida de 48V de los relés de activación de inputs.

De momento no lo podemos obtener, ya que estamos a la espera de que llegue el módulo octoacoplado de relés controlado por la RPI. Hemos usado en su lugar un módulo Arduino que el departamento desarrolló en su momento para generar señales de activaciones en las  IPTUs. Está limitado a un solo canal y no disponemos de señal de feedback (T0). Se ha tomado como instante sustituto T1, timestamp proporcionado por el mismo equipo mediante protocolo SNMP (se esperan 700us que no podemos contabilizar del retardo T1 – T0.

  - T1, INP (TPU A): Instante en el que llega la interrupción de la señal de activación del input al módulo IPTU.

  - T2, TX (TPU A): Instante en el que el modulo de procesamiento MWTU ya ha procesado el input y generado la orden, y la envía a través del módulo de comunicación asignado (ICPT para estas pruebas).

  - T3, RX (TPU B): Instante en el que se recibe la orden de disparo en el modulo de comunicación ICPT.

  - T4, OUTP: Instante en el que el módulo MWTU ya ha procesado la orden de disparo y se genera el Output a través del modulo IPTU.

  - T5: Llegada del Output a la Raspberry a través de un PIN GPIO en modo PullUp.

*T0 y T5 se obtienen de los logs generados por la propia RPI.
*T1, T2, T3 y T4 se extraen de los traps SNMP capturados por cada equipo. Estos timestamps dependen del reloj configurado por cada equipo. En nuestro caso, tenemos las dos TPUs y la RPI sincronizadas con el reloj que dispone el servidor NTP de nuestro departamento.

Incidente:

Cuando tenía todo listo para ejecutar las pruebas de rendimiento, los relojes de los equipos TPU-1 no sincronizaban bien, aun utilizando el mismo reloj del servidor local de ZIV. Descubrimos que era un problema del hardware empleado en uno de los equipos. Al mezclar una de las MWTUs de un equipo (módulo de procesamiento, donde esta el micro CPU de la TPU-1) con otra versión diferente (más actualizada con el submódulo KWTU), una de ellas mantenía un retardo de 5ms que descuadraba todos los resultados. Una vez montado el mismo tipo de MWTU y actualizado sus firmwares a las últimas versiones, se logró obtener una correcta sincronización en los timestamps de los traps SNMP (de donde obteníamos el instante exacto de cada interrupción) procedente de cada equipo.

## Work Plan modifications

Significant modifications to the Work Plan are required due to two main factors:

- Hardware Delays (WP2): The diagnosis of the leakage issue and the procurement of the necessary optocouplers have paused the physical validation phase of the HIL system. A delay of approximately 1-2 weeks is estimated for component arrival and assembly.

- Scope Expansion (New WP3 - Noise Injection): Following technical feedback, the project scope has been expanded to include a dedicated Noise Injection and Robustness Phase. This was previously a high-level goal but now requires specific hardware and software development not accounted for in the original plan:

  - Analog Domain: Design of an operational amplifier-based circuit (Summer/Amplifier) to mix TPU signals with white noise for IBTU module testing.

  - Digital Domain: Integration of an external Netstorm (Albedo) equipment for Ethernet impairment testing.

Consequently, the original "WP3 Integration" will be shifted to become "WP4", and a new "WP3" focused on Noise & Robustness is introduced.

# updated work plan

## Updated Work Packages, Tasks and Milestones

Work Packages:

| Project: Design and Development of an Automated Test Bench for Robustness Testing of Teleprotection Equipment | WP ref: WP1 |  |
| --- | --- | --- |
| Major constituent: Development of the Control and Testing Software | Sheet 1 of 3 |  |
| Short description: This phase focuses on growing the existing test software. The current Python environment, using Robot Framework and Selenium for web UI testing, will be extended to control the new Hardware-in-the-Loop (HIL) system. This requires adapting the GUI, developing new Python libraries to manage communication with the Raspberry Pi controller, and improving the automated reports. | Planned start date: 06-10-2025 Planned end date: 30-10-2025 |  |
|  | Start event: 06-10-2025 End event: 31-10-2025 (Completed) |  |
| Internal task T1: Analyse the existing Robot Framework and Selenium codebase. Design and implement new Python libraries and keywords to manage communication (e g. via PySerial) with the Raspberry Pi controller. Internal task T2: Modify the current Tkinter graphical user interface to include new controls (buttons, status indicators) for executing Hardware-in-the-Loop tests and visualizing their results in real-time. Internal task T3: Define the logic for the new HIL test cases within Robot Framework, structuring the keywords and sequences that will be used to command the hardware and verify the results. Internal task T4: Extend the automatic report generation capabilities of Robot Framework to include specific results from physical tests, such as hardware command response times and the PASS/FAIL status of HIL validations. | Deliverables: T1 ✓ T2 ✓ T3 ✓ T4 ✓ | Dates: 13-10-2025 21-10-2025 24-10-2025 30-10-2025 |

| Project: Design and Development of an Automated Test Bench for Robustness Testing of Teleprotection Equipment | WP ref: WP1 |  |
| --- | --- | --- |
| Major constituent: Design and Construction of the HIL Test Bench (UPDATED) | Sheet 1 of 3 |  |
| Short description: This phase covers the design and construction of the Hardware-in-the-Loop testbench. A Raspberry Pi 4 will work as the control unit, managing 8-channel relay modules via its GPIO pins. This setup is designed to physically activate the inputs of the TPU-1's IPTU module, replacing the current software-based simulation. | Planned start date: 31/10/2025 Planned end date: 02/12/2025 |  |
|  | Start event: 31/10/2025 End event: In Progress |  |
| Internal task T1: Create the complete circuit and connection diagrams for the HIL system, detailing the wiring between the Raspberry Pi's GPIO pins, logic level converters, 8-channel relay modules, and the input terminals of the TPU-1's IPTU module. Internal task T2: Get all necessary components for the project's shopping list (Raspberry Pi, relays, power supplies, etc.) and physically assemble them into a functional test bench chassis. Internal task T3: Develop and deploy the Python scripts on the Raspberry Pi. These scripts will create a listener (e g. a serial or socket server, like what we built for the SNMP) to receive commands from the main control PC. They will also manage the GPIO pin activations to control the relay module. Internal task T4 (Update): Assembly of the Optocoupler interface and wiring upon arrival. Internal task T5 (Update): Migration of the HIL Server code from RPi.GPIO to lgpio/libgpiod to support Debian 13 interrupts correctly (as discovered during software tests). Internal task T6: Perform independent tests on the assembled HIL bench. Verify that the Raspberry Pi can reliably and activate each relay on command and debug any issues with the electrical connections or controller scripts. Se ha verificado todo el funcionamiento del sistema HIL implementado haciendo uso de un módulo Arduino para generar disparos y activar inputs via Hardware (a la espera de poder hacer lo mismo con el módulo de relés, optoacopladores pendientes de llegar). El sistema se ha preparado y adaptado en previsión de utilizar la propia Raspberry para la generación de inputs. Con el escenario provisional ya se han hecho pruebas de rendimiento mediante ráfagas que funcionan perfecto con el sistema provisional. Solo obtuvimos resultados confusos ante el incidente mencionado por culpa de la corriente de fuga en el módulo de comunicación IPTU. Todos los equipos sincronizan con una precisión de alrededor 1ms su reloj con el del servidor que ZIV dispone y que nos conectamos mediante NTP. | Deliverables: T1 ✓ T2 ✓ T3 ✓ T4 ✓ T5 ✓ T6 | Dates: |

Milestones

| WP# | Task# | Short title | Milestone / deliverable | Date (week) |
| --- | --- | --- | --- | --- |

## Updated Time Plan (Gantt diagram)